DIGITAL PROGRAMMABLE PANEL METERS 96x48

ITI 16–ITI17 PROCESS MEASUREMENTS TEMPERATURE

- Two-colors display 14 mm green/red with possible change of color on alarm or pre-alarm.

- IP65 on the front.

- Scaling in 2 points.

- Linearization from 1 to 21 segments.

- In temperature linearization additionnal of programmable sensors by RS232/485.

- 2 pre-alarm thresholds and 2 alarm thresholds with acknowledgement.

- Memorizing of the minis and the maximum one

- Connection by detachable connector block

ENTRIES

ITI 16

Current of process

Voltage of process

D.C voltage

ITI 17

Temperature

Current of process

Voltage of process

D.C voltage

Resistance

For all the instruments of this series, the programming is very simply carried out using the 3 keys keyboard located on front . For those equipped with an RS232/485, the programming can be carried out using a PC software LTCTM provided with this option, or by any software output using MODBUS.

Process values can be realed either in 2 points,or inearized using from 3 to 22 points(2 to 21 segments)possible Display from -19999 to 99999.

Connections are carried out with the back on screw connectors.

OPTIONS OF EXITS

- 2 alarm relays or

- 2 alarm relays ,analog output 0-10V or 0-20mA and RS232/485 Modbus or ASCII output.

POWER SUPPLY

- 20 to 60 V D.C and 18 to 44 V A.C 47 to 420 Hz or

- 115 to 300 V D.C and 90 to 260 V A.C, 47 to 420 Hz

DIMENSIONS

Format 96 x 48 mm.

Panel cut out in conformity with DIN43700

ITI 16 :Process Signals Measurement

The ITI 16 is intended for the measurement process of voltage and current .

Uncertainty given for one year for a temperature ranging between 18 and 28°C

Input resistance mA : 50Ω Input resistance:

• Range 10 V : 1,11 MΩ.

• Other ranges V : 10 MΩ.

Applicable maximum voltage: 150 V~ .

ITI 17 :Process signals and temperature Measurement

The ITI 17 is intended for measurements of process and temperature by resistive probes and thermocouples.

The software also makes it possible to introduce additional linearizations for the couples B, C, E, L, Mo, N, Pl, R, U and probes JPt100, Ni100, Pt25, Pt50.

Connections are carried out at the back on removable screwing.

Resistance

3 wire : add0,05 % L/Ω of leads.

Temperature by resistor probes

3 wire : add(0,05 % L + 0,15°C)/Ω of leads.

Linearization conforms to the standard INTO 60751/1995 for probe platinum 100 Ω à 0°C, international scale of température EIT 90.

Temperature by thermocouples

Uncertainty due to the internal junction of reference = ± 1°C

Uncertainty due to the use of a junction of reference external (AN8002) = ± 0,2°C typical et 0,5°C maxi.

Linearization conforms to the standard EN 60584-1/1995, international scale of temperature EIT 90.

Possibility to add other thermocouples via software LTCTM

Measurement on potentiometer

ITI 17 makes it possible to measure on potentiometers.

RELAY, ANALOG AND DIGITAL OUTPUTS(OPTIONS)

Thresholds Relay:

In addition of the front LED indication 2 relays for the 2 alarms can be used.

Breaking capacity from the Ä relays/250 V~, 1 250VA ou 5A / 30 V-, 150W max.

Analog exit allowing the copy of measurement output:

Programmable in 0-10 V or 0-20 mA.

- Resistance of load≥ 1 kΩ sur 10 V, ≤ 800 Ω sur 20mA.

- Insulation input/output : 60 V, except if the ITI supplies the sensor • Accuracy: ± (0,1% +5mV ou 10μA).

- 4 000 pts of resolution.

- Programmable in 2 points by the keyboard or software LTCTM with for example.

AnA.LO = 22,00°C pour 0 V ou 0 mA et AnA.HI = 60,55°C pour 10 V ou 20 mA.

Digital display RS232/485

Programmable exit by keyboard allowing.

communication in ASCII or MODBUS RTU for network application.

The instruments connected in network with transmitters or AOIP DATA acquisition systems to a PC equipped with the software of supervision LWTM or LW1 allowing display of measurements in real or remote time in the form of synoptic, curves, numerical bargraphes, tables.

Logiciel LTCTM

Software provided with the ITI equipped with an digital outputl allowing:

- To prepare the programming of the instruments and to store those on PC.

- To add to the instrument linearization additional one of thermocouple (B, C, E, L, Mo, N,Pl, R, U) and one of resistive probe (JPt100, Ni100, Pt25, Pt50).

Software provided on a floppy disk also containing instruction manual, a text file about communication in Modbus and of the ASCII orders.

GENERAL CARACTERISTIQUES

- Reference23 domain ± 5°C (45 à 75% de HR), temperature coefficient <10% precision/°C.

Operating domain to 50°C (20 à 80% HR without condensation).

Limits operation domain- 10°C à + 50°C. Storage temperatures limit - 30°C à + 70°C.

- Safety: apparatus conforms to the European standard EN 61010-1. Category II, pollution 2.

Tension of assignment compared to the ground:

Measurement input 150 V Analog output or output RS232/RS485 60 V Relay output 250 V.

-EMC and Emission: EN 55022/1994, class B.

Immunity: IN 50082-1/1992

Condusted: IEC 801-3/1984.

Condusted: IEC 801-4/1988.

Electrostatic discharges: IEC 801-2/1991.

- Weight 160g.

INSTRUCTIONS TO ORDER

Accessories

AN8002 Compensation of external cold junction.

Er42062-001 Circuit protective RC for contact relay.